ELECTRICAL WORK	 DIVISION 26

Section 260800

Commissioning ELECTRICAL EQUIPMENT

# GENERAL

## DESCRIPTION OF WORK

### This section applies to startup, testing, and commissioning of the Electrical System.

#### Reference Division One, Section 01-91-13 for additional requirements

#### Coordination and participation of the commissioning of the Mechanical and BAS systems.

#### Assisting the Commissioning Authority to develop, edit, and document system operation descriptions.

#### Providing qualified personnel to execute commissioning tests approved or written by the Commissioning Authority (CxA), including seasonal testing required after the initial commissioning as specified in this specification.

#### The Division 26 subcontractor shall take the lead responsibility for inspecting, completing, and documenting the Pre-Functional Testing for the Electrical Systems to ensure the systems are fully operational and ready for Functional Testing.

#### Assist in completing and endorsing mechanical checklist items on Pre-Functional Test forms for Division 23 equipment and systems to ensure the systems are fully operational and ready for functional testing.

#### The Division 26 subcontractor shall take the lead responsibility for demonstrating the operations of the Electrical Systems for the Functional Tests.

#### Provide equipment, materials, and labor necessary to correct deficiencies found during the commissioning process, which fulfill contract and warranty requirements.

#### Providing operation and maintenance information and record drawings to the Commissioning Authority for review, verification and organization, before the start of training.

#### Providing training for the systems specified in this Division, with coordination by the Commissioning Authority.

#### Automated Electrical Control Systems

#### Validate all lighting controls, sequences, dimming, and operation

#### Validate and document the operation of all electrical receptacles that are controlled

#### Validate and document all electrical metering systems used to monitor building energy use and control to improve overall building efficiency

### Commissioning is a multi-tiered activity with several levels. These levels are further detailed in the Commissioning Plan provided by the Commissioning Authority (CxA). The CxA will provide oversight and will lead all Functional Performance Testing described in the Commissioning Plan. The Contractor will assist the CxA during the Functional Performance Testing of each piece of equipment and/or system.

### Electrical commissioning is primarily the responsibility of the Division 26 subcontractor; however, it is led under the guidance and approval of the CxA. The commissioning process does not diminish the subcontractor's role and obligations to complete all portions of the work in a satisfactory and fully operational manner.

### The Contractor is specifically required to provide the following to aid the CxA and ensure system conformance and operation:

#### Provide skilled technicians to start up and debug all systems within this Division of work.  These same technicians shall be made available to assist the Commissioning Authority in completing the commissioning program as it relates to each system and their technical specialty. Work schedules and the time required for testing will be requested by the Commissioning Authority and coordinated by the Subcontractor. The Subcontractor shall ensure that the qualified technician(s) are available and present during the agreed-upon schedules and of sufficient duration to complete the necessary tests, adjustments, and/or problem resolutions.

#### System problems and discrepancies may require additional technician time, Commissioning Authority time, redesign, and/or reconstruction of systems and their components.  The additional technician time shall be made available for the subsequent commissioning periods until the required system performance is obtained.

#### The Commissioning Authority reserves the right to judge the appropriateness and qualifications of the technicians relating to each item of equipment, system, and/or sub-system. The qualifications of technicians include expert knowledge of the specific equipment involved, adequate documentation and tools to service and commission the equipment, and an attitude and willingness to work with the Commissioning Authority to get the job done.  A liaison or intermediary between the Commissioning Authority and qualified factory representatives does not constitute the availability of a skilled technician for purposes of this work.

#### Lead the team in demonstrating the operations of the Electrical Systems to complete the Functional Test documentation.

#### Participate in Commissioning Mechanical, Electrical, and BAS meetings organized by the Commissioning Authority and General Contractor.

#### Provide any manufacturer’s testing reports for components of the Mechanical Systems and attach these reports to the appropriate completed FIV Test forms.

## Scheduling

### Commissioning shall comply with the Construction Contract schedule.  Cooperate with the Commissioning Authority in the following manner:

#### Allow sufficient time before final completion dates so that test and balance and commissioning testing can be accomplished.

#### Provide labor and material to make corrections when required without undue delay.

## Work to resolve deficiencies

### In some systems, maladjustments, misapplied equipment, and/or deficient performance under varying loads will result in additional work being required to commission the systems.  This work will be completed under the direction of the Owner, with input from the General Contractor, equipment supplier, and Commissioning Authority.  While all members will have input and the opportunity to discuss, debate, and work out problems, the Engineer of Record will have final jurisdiction over the necessary work to be done to achieve the desired performance.

### Corrective work shall be completed in a timely fashion to permit the timely completion of the commissioning process.  Experimentation to render system performance will be allowed.  If the Commissioning Authority deems the experimentation work to be ineffective or untimely in relation to the commissioning process, the Commissioning Authority will notify the Owner, specifying the nature of the problem, the expected steps to be taken, and the deadline for completing the activities.  If the deadline(s) pass without resolution of the situation, the Owner reserves the right to obtain supplementary services and/or equipment to resolve the issue. Costs incurred to solve the problems expeditiously will be the Subcontractor's responsibility.

### Provide a written response within two weeks of receipt of any corrective action items noted by the CxA.

## SUBMITTAL REVIEW

### The commissioning agent shall review all electrical equipment submittals for commissionability. This is not a replacement of the engineer of records review, nor shall it be considered an acceptance of said submittal.

### The CxA shall request submittals for review, and the contractor shall be responsible for the timely receipt of all shop drawings and other necessary materials.  Any anticipated delays shall be immediately communicated to the CxA, Owner, and all other affected parties.

## INSTALLATION VERIFICATION

### Before performing the startup verification, all pre-commissioning checklists must be complete.  No functional performance testing shall be executed until work included in this section is completed.

### The contractor shall ensure that all construction debris and dirt have been removed and that all systems, where applicable, have been cleaned.

### The contractor shall inspect all equipment and systems that have been put into service and are functioning.  All devices shall have been calibrated, and all control loops shall have been tuned.

### Systems shall break down all checklists according to the format shown in the Commissioning Plan and Submittal Review.

### FIV’s shall be provided to the contractor by the CxA.

## COORDINATION

### Coordinate services with the work of various trades to ensure rapid completion of services.

END OF SECTION